## Slide 1: ATAC: Ambient Temperature-Aware Capping for Power Efficient Datacenters
Georgia Tech
MARS Lab
Sungkap Yeo
Mohammad M. Hossain
Jen-cheng Huang
Hsien-Hsin S. Lee
Notes: Presentation performed by Sungkap Yeo on Tuesday, Nov, 4, 2014
09:50am-11:30am

## Slide 2: Executive Summary
Observation ▷ Server locations are not created equal. ‘Minority’ of servers ‘rarely’ experience thermal emergencies.
Goal ▷ Reduce cooling power & avoid thermal overshooting on CPUs
Solution ▷ Inlet temperature-aware technique
Results
  38% savings in cooling power
  <1% performance degradation
2
Notes: 2

## Slide 3: Datacenters
3
Cloud computing
2 ~ 10%
Notes: 3

## Slide 4: Datacenters
4
Servers
Networking
Storage
Power delivery
Cooling
Notes: 4

## Slide 5: Datacenters: Traditional
5
Servers
Networking
Storage
Power delivery
~50%
Cooling
~50%
Notes: 5

## Slide 6: Datacenters: State-of-the-art
6
Servers
Networking
Storage
Power delivery
>90%
Cooling
<10%
Notes: 6

## Slide 7
Datacenters: State-of-the-art
“Parasol and Greenswitch: Managing datacenters powered by renewable energy”

## Slide 8
Datacenters: State-of-the-art
Google datacenter in Finland

## Slide 9
Datacenters: State-of-the-art
Yahoo datacenter

## Slide 10
Datacenters: Majority
Small to medium datacenters
  Responsible for more than 70% of the entire electrical power used by datacenters
  Still labor under heavy cooling overhead about 50%
  More demand: private cloud

## Slide 11
11
11
Datacenter Cooling Essentials
Motivation
Our Approach: ATAC
Evaluation
Notes: 11
11

## Slide 12: Datacenter Cooling Essentials
Two things
  Control algorithms for cooling units
  Cool air delivery time
12

## Slide 13: Datacenter Cooling Essentials (1)
13
Static control algorithm
  Always supplies cool air based on worst case scenario
  Not efficient
Dynamic control algorithm
  Starts from static control algorithm
  While all servers are under emergency temperature, raises room temperature
  When any server experiences emergency temperature, lower room temperature

## Slide 14: Datacenter Cooling Essentials (2)
Cool air delivery time
  Why is it important?
14
Feeling
Hungry
Order a Pizza
Remain hungry!

## Slide 15: Datacenter Cooling Essentials
Hottest server
15
Cooling unit

## Slide 16: Datacenter Cooling Essentials
Hot
Inlet air temperature < Emergency temperature
16

## Slide 17: Datacenter Cooling Essentials
Hot
!
Inlet air temperature > Emergency temperature
17
Temperature margin is required
for all dynamic control algorithms!

## Slide 18
18
18
Datacenter Cooling Essentials
Motivation
Our Approach: ATAC
Evaluation
Notes: 18
18

## Slide 19: ATAC ▷ Motivation I
Chart: Inlet Temperature (°C)
| 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35
Instant delivery of cool air is assumed | 1145585830 | 834500070 | 1070927560 | 1324083300 | 1359561840 | 1173640620 | 2690665860 | 1978013150 | 983819610 | 866710160 | 1476423870 | 2162613130 | 0 | 0 | 0 | 0 | 0 | 0
Non-zero delivery of cool air is assumed | 1141489550 | 838428310 | 1091846190 | 1312287900 | 1349099830 | 1174027970 | 2696601990 | 1972724760 | 984124010 | 909794860 | 1421874820 | 2004672800 | 169140110 | 80560 | 26110 | 13560 | 4800 | 710
Thermal overshooting
Non-zero delivery time of cool air
Inlet air temperature > Temergency
19
About 1% of the time

## Slide 20: ATAC ▷ Motivation II
Chart: Height of Server Chassis in Racks
| Lowest | Lower | Middle | Higher | Highest
 | 15.977 | 17.7024 | 19.8475 | 27.702 | 33.1725
 | 15.2731 | 17.398 | 22.1272 | 27.2635 | 34.5544
 | 16.1901 | 18.2555 | 21.9552 | 31.1976 | 35.1826
 | 15.2558 | 15.8174 | 18.4675 | 20.2958 | 30.6795
 | 15.2322 | 15.1688 | 16.2787 | 20.901 | 32.1987
 | 15.2422 | 15.1869 | 16.3438 | 21.2555 | 32.9519
 | 15.2774 | 15.769 | 18.3106 | 22.6944 | 33.684
 | 16.1933 | 17.7744 | 20.139 | 27.9213 | 33.4058
 | 15.2508 | 17.1654 | 21.6577 | 25.6689 | 32.6828
 | 16.0697 | 17.6761 | 19.4143 | 26.7694 | 32.5521
Thermal overshooting
Only for the small numbers of servers
20

## Slide 21: ATAC ▷ Motivation
Potential solutions should
  perform locally AND
Non-zero delivery time of cool air
Only for the small numbers of servers
  take inlet air temperature into account
21
Goal
  Keep CPU temperature under the target temperature even when Tinlet air > Temergency

## Slide 22
22
22
Datacenter Cooling Essentials
Motivation
Our Approach: ATAC
Evaluation
Notes: 22
22

## Slide 23: Our approach: ATAC
Experiments: Server power vs. Inlet air temperature
23
Chart: Inlet Air Temperature (°F)
| 80 | 82 | 84 | 86 | 88 | 90 | 92 | 94 | 96 | 98 | 100
Other Parts (W) | 202.6188 | 203.655 | 203.1382 | 204.2647 | 203.152 | 202.739 | 203.7555 | 204.2555 | 204.2555 | 205.2555 | 205.2555
Fans (W) | 11.3812 | 13.345 | 16.3618 | 18.7353 | 21.848 | 25.261 | 28.7445 | 28.7445 | 28.7445 | 28.7445 | 28.7445
Fans = Max

## Slide 24: Our approach: ATAC
Chart: Inlet Air Temperature (˚C)
| 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39
3.1Ghz | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 73 | 74 | 75 | 76 | 77 | 78
2.9Ghz | 71 | 71 | 70 | 71 | 71 | 71 | 70 | 70 | 71 | 72 | 73 | 74 | 75
2.7Ghz | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 70 | 70 | 71 | 72 | 73
Repeating experiments with different configurations
24
Chart: Inlet Air Temperature (˚C)
| 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39
3.1Ghz | 214 | 217 | 219.5 | 223 | 225 | 228 | 232.5 | 233 | 233 | 234 | 234 | 234 | 235
2.9Ghz | 202 | 204 | 206 | 210 | 213 | 216 | 218.5 | 224 | 228 | 229.5 | 230 | 230 | 231
2.7Ghz | 201 | 205 | 206 | 208 | 210 | 212 | 214 | 217 | 222 | 223.5 | 223.5 | 224 | 224
Core temperature can be under the control
even after Temergency
Linear model

## Slide 25
ATAC is a system-level technique
  Throttles performance when Tinlet air > Temergency
  Any theory that explains our experiments?
Fan affinity laws [22]
  Watts (heat transfer) ∝ ΔTemperature × Amount of air
constant
  CPU power ∝ (Tcore － Tinlet air)
25
Old CPU Power
New CPU Power
Old ΔTemperature
New ΔTemperature
＝
Our approach: ATAC

## Slide 26: ATAC: Algorithm

## Slide 27: ATAC ▷ Configurables
Aggressive ATAC
  ATAC compromises performance to reduce CPU power consumption.
  How aggressively?
ATAC－#
  ATAC－0
    Lower CPU performance when Tinlet air = Temergency
  ATAC－X
    Lower CPU performance when Tinlet air = Temergency －X
27

## Slide 28
28
28
Datacenter Cooling Essentials
Motivation
Our Approach: ATAC
Evaluation
Notes: 28
28

## Slide 29: ATAC ▷ Simulation Setup
29
Raised Floor
Hot Aisle
Cold Aisle
Hot Aisle
(a) Bird's-eye view
(b) Top view
CRAC
Racks
Racks

## Slide 30: ATAC ▷ Simulation Setup
Google cluster data (GCD)
  select 5 days
12,800 processing cores
  50 blade chassis
  16 servers per blade chassis
  16 processing cores
    AMD Opteron 6386 SE, 140W TDP
30

## Slide 31: ATAC ▷ Evaluation
Baseline
  Dynamic cooling control Temergency ＝ 40ºC that targets Tcore ≤ 80ºC
  No safety margin
  Failed because of non-zero cool air delivery time
31

## Slide 32: ATAC ▷ Evaluation
ATAC, DTM, Power capping, and PowerNap
32

## Slide 33: ATAC ▷ Evaluation
ATAC, DTM, Power capping, and PowerNap
33

## Slide 34: ATAC ▷ Key Contributions
34
Ambient temperature-aware thermal control
Negligible performance degradation
No need for the safety margin
38% saving in cooling power
<1%

## Slide 35
Georgia Tech
MARS Lab
http://arch.ece.gatech.edu
ATAC: Ambient Temperature-Aware Capping for Power Efficient Datacenters
Sungkap Yeo
Mohammad M. Hossain
Jen-cheng Huang
Hsien-Hsin Sean Lee
Notes: 35